# Corrected Mathematical Formulation of the Current HVAC Framework

Q1-journal-ready replacement methodology section

# Editorial note

This section reports the equations that are actually implemented in the current hvac_v3_engine.py configuration. It intentionally describes Strategy S3 as condition-based maintenance combined with continuous online control optimization. It does not describe S3 as forecast-based predictive maintenance, because no future degradation horizon or remaining-useful-life model is currently used in the maintenance decision.

The present default configuration also activates a dynamic reduced-order thermal model, monthly component corrections, and a rule-based operational-state correction layer. These layers must be reported because they modify the final energy values used by the S3 objective function. Optional modules that are disabled by default are not presented as active parts of the reported formulation.

# 1. Design quantities

The nominal cooling capacity, heating capacity, airflow rate, maximum occupant count, and maximum internal electrical gain are calculated from the conditioned floor area, A.

Equation (1): nominal cooling capacity

Qc,des=A qc,A1000

Equation (2): nominal heating capacity

Qh,des=A qh,A1000

Equation (3): nominal airflow rate

Vair,nom=A vair,A

Equation (4): maximum occupant count

Nmax=A ρocc

Here, qc,A and qh,A are the area-normalized design cooling and heating intensities in W m​−2, vair,A is the airflow rate in m​3 h​−1 m​−2, and ρocc is the occupant density in person m​−2.

# 2. Occupancy and internal gains

At time step t, the effective occupant count is

Equation (5): occupant count

Nt=Nmax ot

where ot is the calendar- and hour-dependent occupancy fraction.

Lighting and equipment powers are

Equation (6): installed lighting and equipment powers

PL=A pL,A1000,  PE=A pE,A1000

The internal electrical gain used by the load model is

Equation (7): internal electrical gain

Qint,t=PL+PEmax0.20, 0.20+fuseot

The sensible occupant gain is

Equation (8): sensible occupant gain

Qocc,t=Nt qsens1000

# 3. Static cooling and heating loads

The cooling and heating temperature differences are

Equation (9): temperature differences

ΔTc,t=maxTa,t−Tsp,t,0,  ΔTh,t=maxTsp,t−Ta,t,0

The normalized solar term and humidity multiplier are

Equation (10): solar and humidity modifiers

gt=clipGHIt700,0,1.5

μRH,t=1+kRHmaxRHt−60,0

For a daily simulation, the seasonal solar factor is

Equation (11): daily solar-season factor

st=maxsinπdt365,0

For a sub-daily simulation, the code uses st=1 because the uploaded or generated irradiance series already contains the diurnal variation.

The static cooling-load components are

Equation (12): envelope cooling load

Qc,env,t=χenv ac Qc,desΔTc,tΔTc,ref

Equation (13): solar cooling load

Qc,sol,t=χsol fsol Qc,des gt st

Equation (14): infiltration cooling load

Qc,inf,t=χinf finf,c Qc,desΔTc,tΔTc,ref

The resulting static cooling load is

Equation (15): total static cooling load

Qc,stat,t=Qc,env,t+Qc,sol,t+Qint,t+Qocc,t+Qc,inf,tμRH,t+Qlat,t

where Qlat,t=0 in the present default configuration because latent-load coupling is disabled by default.

The static heating-load components are

Equation (16): envelope and infiltration heating loads

Qh,env,t=χenv ah Qh,desΔTh,tΔTh,ref

Qh,inf,t=χinf finf,h Qh,desΔTh,tΔTh,ref

The internal-gain credit is

Equation (17): internal heating credit

Qcredit,t=fcreditQint,t+Qocc,t

and the static heating demand is

Equation (18): total static heating load

Qh,stat,t=Qh,env,t+Qh,inf,t−Qcredit,t

# 4. Dynamic reduced-order thermal layer

The current default configuration activates a two-state reduced-order dynamic layer. The equivalent zone-air and thermal-mass capacitances are

Equation (19): thermal capacitances

Cz=A cz,  Cm=A cm

The effective envelope heat-transfer coefficient is

Equation (20): effective envelope coefficient

Henv=12acQc,desΔTc,ref+ahQh,desΔTh,reffUA

The ventilation/infiltration coefficient and mass-zone coupling coefficient are

Equation (21): ventilation and mass-coupling coefficients

Hvent=ACH V ρair cp,air3600fvent

Hmz=A hmz1000

where V=Ahf is the building air volume.

The free-floating zone temperature is calculated as

Equation (22): free-floating zone temperature

Tz,tfree=Tz,t+ΔtCzHenv+HventTa,t−Tz,t+HmzTm,t−Tz,t+Qsol,a,t+Qint,a,t

The dynamic cooling and heating demands are

Equation (23): dynamic thermostat demands

Qc,dyn,t=maxTz,tfree−Tc,spCzΔt,0

Qh,dyn,t=maxTh,sp−Tz,tfreeCzΔt,0

The accepted zone temperature and next thermal-mass temperature are

Equation (24): state update

Tz,t+1=clipTz,tfree−εQc,dyn,tΔtCz+εQh,dyn,tΔtCz,Tmin,Tmax

Tm,t+1=clipTm,t+ΔtCmHmzTz,t+1−Tm,t+Qsol,m,t+Qint,m,t+0.15HenvTa,t−Tm,t,Tmin,Tmax

Correction for Word insertion: in the second expression above, the term must read

HmzTz,t+1−Tm,t

without any additional symbol before Hmz.

The static and dynamic loads are blended using the replacement fraction βRC:

Equation (25): blended cooling and heating loads

Qc,RC,t=1−βRCmaxQc,stat,t,0+βRCQc,dyn,t

Qh,RC,t=1−βRCmaxQh,stat,t,0+βRCQh,dyn,t

The current default value is βRC=0.75.

# 5. Monthly availability and minimum operational loads

The present default configuration applies month-dependent availability factors:

Equation (26): monthly availability correction

Qc,av,t=ac,mQc,RC,t,  Qh,av,t=ah,mQh,RC,t

The occupancy factor used by the minimum-load calculation is

Equation (27): minimum-load occupancy factor

focc,t=clip1−wo+woot,0.25,1.20

The month-specific minimum operational loads are

Equation (28): minimum operational loads

Qc,min,t=rc,mQc,desfocc,tac,m

Qh,min,t=rh,mQh,desfocc,tah,m

The accepted pre-capacity loads are

Equation (29): accepted operational loads

Qc,op,t=maxQc,av,t,Qc,min,t

Qh,op,t=maxQh,av,t,Qh,min,t

These empirical monthly terms are calibration terms and must be identified as such in the manuscript. They are not universal physical constants.

# 6. Physical degradation model

Let τ=Δt/24 be the time-step duration in days. Heat-exchanger fouling resistance is updated as

Equation (30): fouling-resistance update

Rf,t+1=Rf*−Rf*−Rf,texp−Bfτ

Filter dust accumulation is

Equation (31): filter-dust update

md,t+1=md,t+md αtτ

The resulting pressure drop is

Equation (32): filter pressure drop

ΔPt+1=minΔPclean+kclogmd,t+1,ΔPmax

The composite degradation indicator currently implemented in the code is

Equation (33): implemented composite degradation indicator

δt+1=12Rf,t+1Rf*+12ΔPt+1ΔPmax

This is the exact implemented equation. It does not equal zero at a clean filter. With the current defaults, ΔPclean=150 Pa and ΔPmax=450 Pa, giving δclean=0.1667. The manuscript must not claim that the current δ is a zero-to-one percentage of deterioration.

# 7. Degradation-dependent coefficient of performance

The implemented cooling coefficient of performance is

Equation (34): cooling COP

COPc,t=minCOPc,nom,max0.8,COPc,nom−kageyt1+0.45Rf,t/Rf*1−0.018maxTa,t−25,0

The implemented heating coefficient of performance is

Equation (35): heating COP

COPh,t=minCOPh,nom,max0.8,COPh,nom−0.6kageyt1+0.30Rf,t/Rf*1−0.010max18−Ta,t,0

# 8. HVAC, fan, pump, and auxiliary powers

Under the current default dominant-mode setting, the active thermal load is the larger branch that exceeds its minimum activation threshold. The corresponding HVAC electrical power is

Equation (36): thermal HVAC electrical power

PHVAC,t=QHVAC,tCOPt

where COPt is selected from Equation (34) or Equation (35) according to the dominant operating mode.

The raw fan power is

Equation (37): raw fan power

Pfan,raw,t=Vair,nomαt/3600ΔPt1000ηfan

The default model also applies a schedule-based fan floor. Let

Equation (38): fan runtime and airflow floors

rfan,t=clipmaxrmin,woccot+wHVACIHVAC,tafan,m,0,1.25

αfloor,t=maxαt,αmin,fan

Then

Equation (39): schedule-based fan power

Pfan,sch,t=Pfan,des,tmaxrfan,t,αfloor,t

Pfan,t=maxPfan,raw,t,Pfan,sch,t

where

Pfan,des,t=Vair,nom/3600ΔPt1000ηfan

Because detailed water-side pressure coupling is disabled by default, pump and auxiliary powers are

Equation (40): pump and auxiliary powers

fop,t=maxot,0.35

Ppump,t=A ppump,A1000fop,t1+0.30δt

Paux,t=A paux,A1000fop,t

# 9. Seasonal and operational-state component corrections

The final reported powers are not the raw component powers. The default configuration applies a damped monthly factor to each component j:

Equation (41): monthly component factor

Fj,m=clip1+λsFj,mraw−1,Fmin,Fmax

Pj,ts=Fj,mPj,traw

A rule-based operating regime rt is then assigned, and a second damped factor is applied:

Equation (42): operational-state factor

Gj,rt=clip1+λoGj,rtraw−1,Gmin,Gmax

Pj,tfinal=Gj,rtPj,ts

These correction factors were introduced to reduce residual seasonal mismatch against the reference simulation. They must be reported as calibration layers, and their values and calibration dataset must be made available for reproducibility.

The final total power and period energy are

Equation (43): final power and energy

Ptot,t=PHVAC,tfinal+Pfan,tfinal+Ppump,tfinal+Paux,tfinal

Et=Ptot,tΔt

Carbon emissions are

Equation (44): operational carbon

MCO2,t=Et EFgrid

# 10. Comfort indicator

The current empirical zone-temperature indicator is

Equation (45): calculated zone-temperature indicator

Tz,ind,t=Tsp,t+2.21−αtot+0.08maxTa,t−Tsp,t,0−0.06maxTsp,t−Ta,t,0+kRH,cmaxRHt−60,0+0.60δtot+Pcap,t

where the unmet-capacity penalty is

Equation (46): capacity penalty

Pcap,t=0.015Qunmet,tQc,des100

The comfort deviation used by the objective is

Equation (47): comfort deviation

DT,t=Tz,ind,t−Tset

This variable is an empirical comfort-deviation indicator. It is not PMV, PPD, operative temperature, or an ASHRAE 55 compliance calculation and should not be described as such.

# 11. S3 objective function

The S3 control vector is

Equation (48): decision vector and bounds

xt=Tsp,tαt

Tsp,min≤Tsp,t≤Tsp,max,  αmin≤αt≤αmax

The normalized terms used by the current code are

Equation (49): implemented normalized indicators

et=Et1.5Qc,desΔt

dt=δt

ct=DT,t3

gt=MCO2,t1.5Qc,desEFgridΔt

The implemented objective is

Equation (50): S3 objective

Jt=wEet+wDdt+wCct+wGgt

The default weights are

wE,wD,wC,wG=0.35,0.25,0.25,0.15

Because MCO2,t=EtEFgrid and EFgrid is constant, the code gives

Equation (51): energy-carbon dependence

gt=et

Therefore, the current objective is algebraically equivalent to

Jt=0.50et+0.25dt+0.25ct

The manuscript should disclose this dependence rather than claim four independent optimization objectives.

# 12. S3 stochastic control search

The current search routine is an iterative elite Gaussian stochastic search. It should not be identified as a published APO algorithm unless the actual APO operators are implemented and verified.

The initial centre and standard-deviation vector are

Equation (52): initial search distribution

μ0=Tsp,t−1αt−1,  σ0=1.40.18

A random candidate is generated as

Equation (53): candidate generation

xk,i=clipμk+σk⊙εk,i

where

εk,i∼N0,I

The candidate set also includes the current best solution, the nominal control Tset,1, and the previous accepted control.

After objective evaluation, the elite set contains

Equation (54): elite-set size

Ne=max3,Np4

The search centre and spread are updated as

Equation (55): elite update

μk+1=1Nei∈Ek​xk,i

σk+1=0.72σk

The current stopping rule is a fixed iteration count:

k=Niter

with Np=18 and Niter=10 by default. No convergence tolerance or early-stopping rule is currently implemented.

# 13. S3 condition-based maintenance

S3 control optimization is executed at every simulation time step. Maintenance is subsequently initiated from the current condition indicators.

The heat-exchanger cleaning decision is

Equation (56): heat-exchanger maintenance trigger

uHX,t=1,Rf,t≥Rf,warn or δt≥δtrig0,otherwise

The filter replacement decision is

Equation (57): filter maintenance trigger

uF,t=1,ΔPt≥ΔPwarn or δt≥δtrig0,otherwise

For the physics-based branch, the current maintenance model applies idealized complete restoration of the affected state:

Equation (58): implemented maintenance restoration

Rf,t+=0 when uHX,t=1

md,t+=0 when uF,t=1

The current code does not include maintenance downtime, minimum maintenance intervals, action-specific recovery efficiency, crew availability, or a forecasted failure horizon. These elements belong in future work unless they are first implemented and the scenario matrix is rerun.

# 14. Cost accounting

Period energy cost is

Equation (59): energy cost

CE,t=pEEt

Maintenance cost is

Equation (60): direct maintenance cost

CM,t=uF,tCF+uHX,tCHX

The reported total cost is

Equation (61): total period cost

Ctot,t=CE,t+CM,t

The current maintenance cost is included in the reported total cost but is not included in the S3 objective function. Therefore, S3 does not currently perform joint economic optimization of control and maintenance timing.

# 15. Honest scope statement for the manuscript

The current contribution should be described as follows:

Strategy S3 combines continuous time-step-level optimization of the zone temperature setpoint and airflow fraction with threshold-based condition monitoring of heat-exchanger fouling and filter pressure drop. The strategy is condition-based rather than forecast-based: maintenance actions are initiated from current simulated condition indicators, and no remaining-useful-life or future degradation horizon is used. The control search is implemented as an iterative elite Gaussian stochastic search with a fixed population and iteration count.

The following developments must be presented as future research, not as capabilities of the current study:

- forecast-horizon predictive maintenance;

- CatBoost prediction inside the S3 control or maintenance loop;

- remaining-useful-life estimation;

- maintenance downtime and capacity unavailability;

- incomplete and action-specific maintenance recovery;

- minimum service intervals and maintenance-resource constraints;

- independent carbon optimization using time-varying grid intensity;

- fixed reference bounds for all objective terms;

- formal implementation and benchmarking of a published APO algorithm.

# 16. Pre-submission implementation warning

The current physics-based simulation evaluates degradation before the maintenance decision and then re-evaluates the same period after the maintenance reset. This can advance the degradation equations twice for the reported period while the propagated state follows a different update path. The final numerical results, tables, and claimed savings should not be submitted until the state update is corrected to occur exactly once per accepted time step and the complete scenario matrix is regenerated.