# Nomenclature and Equation References

Corrected HVAC reduced-order degradation framework

Editorial note. The table uses unambiguous recommended manuscript notation. In particular, γGHI,t replaces the first use of gₜ, nd,t replaces the day-of-year use of dₜ, and overbarred objective indicators replace eₜ, dₜ, cₜ, and gₜ. This removes symbol collisions in the earlier equation draft. Units marked “–” are dimensionless.

# 1. Nomenclature

| Category | Symbol | Definition | SI unit | Equation(s) | Implementation note |
| --- | --- | --- | --- | --- | --- |
| Indices and operators | t | Simulation time-step index | – | 5–61 |  |
| Indices and operators | k | Stochastic-search iteration index | – | 52–55 |  |
| Indices and operators | i | Candidate-solution index | – | 53–55 |  |
| Indices and operators | j | Energy component index: HVAC, fan, pump, or auxiliary | – | 41–43 |  |
| Indices and operators | m | Calendar month index | – | 26–29, 38, 41 |  |
| Indices and operators | rₜ | Rule-based operational-state label assigned at time step t | – | 42 |  |
| Indices and operators | Δt | Simulation time-step duration | h | 22–25, 43, 49 |  |
| Indices and operators | τ = Δt/24 | Simulation time-step duration expressed in days | day | 30–31 |  |
| Indices and operators | clip(x,l,u) | Clipping operator that limits x to the interval [l,u] | – | 10, 24, 27, 38, 41–42, 53 |  |
| Indices and operators | max(·), min(·) | Maximum and minimum operators | – | 7, 9–11, 15, 23, 25, 29, 32, 34–35, 38–40, 54 |  |
| Indices and operators | ⌊·⌋ | Floor operator | – | 54 |  |
| Indices and operators | ⊙ | Element-wise vector multiplication | – | 53 |  |
| Indices and operators | 𝒩(0,I) | Multivariate standard normal distribution | – | 53 |  |
| Indices and operators | I | Identity matrix in the Gaussian candidate distribution | – | 53 |  |
| Indices and operators | ℰₖ | Elite candidate set at search iteration k | – | 55 |  |
| Indices and operators | (·)⁺ | State immediately after maintenance restoration | – | 58 |  |
| Indices and operators | (·)raw, (·)(s), (·)final | Raw, seasonally corrected, and final operational-state-corrected quantities | – | 41–43 |  |
| Building and design quantities | A | Conditioned floor area | m² | 1–8, 19, 21, 40 |  |
| Building and design quantities | qᶜ,A | Area-normalized design cooling intensity | W m⁻² | 1 |  |
| Building and design quantities | qʰ,A | Area-normalized design heating intensity | W m⁻² | 2 |  |
| Building and design quantities | Qᶜ,des | Nominal/design cooling capacity | kW | 1, 12–15, 20, 23, 25, 28, 46, 49 |  |
| Building and design quantities | Qʰ,des | Nominal/design heating capacity | kW | 2, 16, 20, 23, 25, 28 |  |
| Building and design quantities | v̇air,A | Area-normalized nominal airflow rate | m³ h⁻¹ m⁻² | 3 |  |
| Building and design quantities | V̇air,nom | Nominal HVAC airflow rate | m³ h⁻¹ | 3, 37, 39 |  |
| Building and design quantities | Nmax | Maximum occupant count | person | 4–5 |  |
| Building and design quantities | ρocc | Occupant density | person m⁻² | 4 |  |
| Building and design quantities | V | Equivalent conditioned air volume | m³ | 21 |  |
| Building and design quantities | hf | Floor-to-floor height used to estimate V = Ahf | m | 21 |  |
| Building and design quantities | ACH | Air infiltration rate | h⁻¹ | 21 |  |
| Occupancy and gains | oₜ | Calendar- and hour-dependent occupancy fraction | – | 5, 7–8, 27, 38, 40, 45 |  |
| Occupancy and gains | Nₜ | Effective number of occupants at time step t | person | 5 |  |
| Occupancy and gains | PL | Installed lighting electrical power | kW | 6–7 |  |
| Occupancy and gains | PE | Installed equipment electrical power | kW | 6–7 |  |
| Occupancy and gains | pL,A | Area-normalized lighting power density | W m⁻² | 6 |  |
| Occupancy and gains | pE,A | Area-normalized equipment power density | W m⁻² | 6 |  |
| Occupancy and gains | fuse | Occupancy-dependent internal-gain use factor | – | 7 |  |
| Occupancy and gains | Qint,ₜ | Internal electrical sensible gain | kW | 7, 15, 17 |  |
| Occupancy and gains | Qsens | Sensible heat released per person | W person⁻¹ | 8 |  |
| Occupancy and gains | Qocc,ₜ | Sensible occupant heat gain | kW | 8, 15, 17 |  |
| Weather and static loads | Ta,ₜ | Outdoor dry-bulb temperature | °C | 9, 22, 34–35, 45 |  |
| Weather and static loads | Tsp,ₜ | Controlled zone temperature setpoint | °C | 9, 45, 48, 52 |  |
| Weather and static loads | ΔTc,ₜ | Positive cooling temperature difference | K | 9, 12, 14 |  |
| Weather and static loads | ΔTh,ₜ | Positive heating temperature difference | K | 9, 16 |  |
| Weather and static loads | GHIₜ | Global horizontal solar irradiance | W m⁻² | 10 |  |
| Weather and static loads | RHₜ | Outdoor relative humidity | % | 10, 45 |  |
| Weather and static loads | γGHI,ₜ | Normalized solar-irradiance modifier; recommended notation replacing the duplicated symbol gₜ | – | 10, 13 |  |
| Weather and static loads | μRH,ₜ | Humidity multiplier applied to the static cooling load | – | 10, 15 |  |
| Weather and static loads | kRH | Cooling-load humidity multiplier coefficient | %⁻¹ | 10 |  |
| Weather and static loads | nd,ₜ | Day-of-year index; recommended notation replacing dₜ to avoid collision with the normalized degradation objective | day | 11 |  |
| Weather and static loads | sₜ | Daily solar-season modifier | – | 11, 13 |  |
| Weather and static loads | χenv, χsol, χinf | Binary activation switches for envelope, solar, and infiltration terms | – | 12–16 |  |
| Weather and static loads | ac, ah | Reduced-order envelope cooling and heating coefficients | – | 12, 16, 20 |  |
| Weather and static loads | ΔTc,ref | Reference cooling temperature difference | K | 12, 14, 20 |  |
| Weather and static loads | ΔTh,ref | Reference heating temperature difference | K | 16, 20 |  |
| Weather and static loads | fsol | Solar cooling-load coefficient | – | 13 |  |
| Weather and static loads | finf,c, finf,h | Cooling and heating infiltration coefficients | – | 14, 16 |  |
| Weather and static loads | Qc,env,ₜ | Envelope component of static cooling load | kW | 12, 15 |  |
| Weather and static loads | Qc,sol,ₜ | Solar component of static cooling load | kW | 13, 15, 22 |  |
| Weather and static loads | Qc,inf,ₜ | Infiltration component of static cooling load | kW | 14–15 |  |
| Weather and static loads | Qlat,ₜ | Latent cooling load; zero when latent coupling is disabled | kW | 15 |  |
| Weather and static loads | Qc,stat,ₜ | Total static cooling load before dynamic RC blending | kW | 15, 25 |  |
| Weather and static loads | Qh,env,ₜ | Envelope component of static heating load | kW | 16, 18 |  |
| Weather and static loads | Qh,inf,ₜ | Infiltration component of static heating load | kW | 16, 18 |  |
| Weather and static loads | fcredit | Fraction of internal gains credited against heating demand | – | 17 |  |
| Weather and static loads | Qcredit,ₜ | Internal-gain heating credit | kW | 17–18 |  |
| Weather and static loads | Qh,stat,ₜ | Static heating demand before dynamic RC blending | kW | 18, 25 |  |
| Dynamic RC model | Cz | Equivalent zone-air thermal capacitance | kWh K⁻¹ | 19, 22–24 |  |
| Dynamic RC model | Cm | Equivalent building-mass thermal capacitance | kWh K⁻¹ | 19, 24 |  |
| Dynamic RC model | cz, cm | Area-normalized zone-air and mass heat capacities | kWh m⁻² K⁻¹ | 19 |  |
| Dynamic RC model | Henv | Effective envelope heat-transfer coefficient | kW K⁻¹ | 20, 22, 24 |  |
| Dynamic RC model | fUA | Multiplier applied to the effective envelope UA term | – | 20 |  |
| Dynamic RC model | Hvent | Ventilation/infiltration heat-transfer coefficient | kW K⁻¹ | 21–22 |  |
| Dynamic RC model | ρair | Air density | kg m⁻³ | 21 |  |
| Dynamic RC model | cp,air | Specific heat capacity of air | kJ kg⁻¹ K⁻¹ | 21 |  |
| Dynamic RC model | fvent | Ventilation heat-transfer multiplier | – | 21 |  |
| Dynamic RC model | Hmz | Thermal coupling coefficient between building mass and zone air | kW K⁻¹ | 21–24 |  |
| Dynamic RC model | hmz | Area-normalized mass-zone coupling coefficient | W m⁻² K⁻¹ | 21 |  |
| Dynamic RC model | Tz,ₜ | Equivalent zone-air state temperature | °C | 22, 24 |  |
| Dynamic RC model | Tm,ₜ | Equivalent building-mass state temperature | °C | 22, 24 |  |
| Dynamic RC model | Tz,ₜfree | Predicted free-floating zone temperature before HVAC action | °C | 22–24 |  |
| Dynamic RC model | Th,sp, Tc,sp | Heating and cooling thermostat setpoints used by the dynamic solver | °C | 23 |  |
| Dynamic RC model | Qsol,a,ₜ, Qsol,m,ₜ | Solar gains assigned to zone air and thermal mass | kW | 22, 24 |  |
| Dynamic RC model | Qint,a,ₜ, Qint,m,ₜ | Internal gains assigned to zone air and thermal mass | kW | 22, 24 |  |
| Dynamic RC model | Qc,dyn,ₜ, Qh,dyn,ₜ | Dynamic cooling and heating demands required to enforce thermostat limits | kW | 23–25 |  |
| Dynamic RC model | ε | Dynamic control effectiveness | – | 24 |  |
| Dynamic RC model | Tmin, Tmax | Lower and upper bounds for dynamic thermal states | °C | 24 |  |
| Dynamic RC model | βRC | Fraction replacing static load with the dynamic RC load | – | 25 |  |
| Dynamic RC model | Qc,RC,ₜ, Qh,RC,ₜ | Cooling and heating loads after static/dynamic blending | kW | 25–26 |  |
| Monthly and calibration layers | ac,m, ah,m | Month-specific cooling and heating availability factors | – | 26, 28 |  |
| Monthly and calibration layers | Qc,av,ₜ, Qh,av,ₜ | Loads after monthly availability correction | kW | 26, 29 |  |
| Monthly and calibration layers | wo | Weight of occupancy in the minimum-load factor | – | 27 |  |
| Monthly and calibration layers | focc,ₜ | Occupancy factor used for minimum operational loads | – | 27–28 |  |
| Monthly and calibration layers | rc,m, rh,m | Month-specific minimum cooling and heating load fractions | – | 28 |  |
| Monthly and calibration layers | Qc,min,ₜ, Qh,min,ₜ | Month-specific minimum operational loads | kW | 28–29 |  |
| Monthly and calibration layers | Qc,op,ₜ, Qh,op,ₜ | Accepted operational loads before capacity limiting | kW | 29 |  |
| Degradation model | Rf,ₜ | Heat-exchanger fouling resistance at time step t | m² K W⁻¹ | 30, 33–35, 56, 58 |  |
| Degradation model | Rf* | Asymptotic/reference fouling resistance | m² K W⁻¹ | 30, 33–35 |  |
| Degradation model | Bf | Fouling growth-rate coefficient | day⁻¹ | 30 |  |
| Degradation model | md,ₜ | Accumulated filter dust mass | kg | 31–32, 58 |  |
| Degradation model | ṁd | Filter dust accumulation rate at unit airflow fraction | kg day⁻¹ | 31 |  |
| Degradation model | αₜ | Normalized airflow/control fraction | – | 31, 37–39, 45, 48, 52 |  |
| Degradation model | ΔPₜ | Filter/system air-side pressure drop used by the degradation model | Pa | 32–33, 37, 39, 57 |  |
| Degradation model | ΔPclean | Clean-filter pressure drop | Pa | 32 |  |
| Degradation model | ΔPmax | Maximum pressure-drop cap | Pa | 32–33 |  |
| Degradation model | kclog | Pressure-drop increase per unit accumulated dust mass | Pa kg⁻¹ | 32 |  |
| Degradation model | δₜ | Implemented composite degradation indicator | – | 33, 40, 45, 49–51, 56–57 |  |
| HVAC performance and power | COPc,nom, COPh,nom | Nominal cooling and heating coefficients of performance | – | 34–35 |  |
| HVAC performance and power | COPc,ₜ, COPh,ₜ | Degradation- and temperature-dependent cooling and heating COP | – | 34–36 |  |
| HVAC performance and power | kage | Annual COP-aging coefficient | year⁻¹ | 34–35 |  |
| HVAC performance and power | yₜ | Elapsed simulated age | year | 34–35 |  |
| HVAC performance and power | QHVAC,ₜ | Active thermal HVAC load under the selected mode | kW | 36 |  |
| HVAC performance and power | COPₜ | COP selected for the active HVAC mode | – | 36 |  |
| HVAC performance and power | PHVAC,ₜ | Thermal HVAC electrical power | kW | 36, 43 |  |
| HVAC performance and power | ηfan | Fan total efficiency | – | 37, 39 |  |
| HVAC performance and power | Pfan,raw,ₜ | Raw pressure-flow fan electrical power | kW | 37, 39 |  |
| HVAC performance and power | rfan,ₜ | Schedule-based fan runtime fraction | – | 38–39 |  |
| HVAC performance and power | rmin | Minimum fan runtime fraction | – | 38 |  |
| HVAC performance and power | wocc, wHVAC | Occupancy and HVAC-activity weights in the fan runtime model | – | 38 |  |
| HVAC performance and power | IHVAC,ₜ | Binary indicator of active thermal HVAC demand | – | 38 |  |
| HVAC performance and power | afan,m | Month-specific fan availability factor | – | 38 |  |
| HVAC performance and power | αmin,fan | Minimum airflow fraction used by the schedule-based fan model | – | 38 |  |
| HVAC performance and power | αfloor,ₜ | Airflow fraction after application of the fan airflow floor | – | 38–39 |  |
| HVAC performance and power | Pfan,des,ₜ | Fan design power at the current pressure drop | kW | 39 |  |
| HVAC performance and power | Pfan,sch,ₜ | Schedule-based fan power floor | kW | 39 |  |
| HVAC performance and power | Pfan,ₜ | Accepted fan electrical power | kW | 39, 43 |  |
| HVAC performance and power | fop,ₜ | Pump/auxiliary operating factor | – | 40 |  |
| HVAC performance and power | ppump,A, paux,A | Area-normalized pump and auxiliary power densities | W m⁻² | 40 |  |
| HVAC performance and power | Ppump,ₜ, Paux,ₜ | Pump and auxiliary electrical powers | kW | 40, 43 |  |
| Corrections, energy, and carbon | Fj,mraw | Raw month-specific calibration factor for component j | – | 41 |  |
| Corrections, energy, and carbon | λs | Damping factor for monthly component calibration | – | 41 |  |
| Corrections, energy, and carbon | Fmin, Fmax | Lower and upper monthly-factor bounds | – | 41 |  |
| Corrections, energy, and carbon | Fj,m | Damped and bounded monthly component factor | – | 41 |  |
| Corrections, energy, and carbon | Gj,rraw | Raw operational-state factor for component j and regime r | – | 42 |  |
| Corrections, energy, and carbon | λo | Damping factor for operational-state correction | – | 42 |  |
| Corrections, energy, and carbon | Gmin, Gmax | Lower and upper operational-state-factor bounds | – | 42 |  |
| Corrections, energy, and carbon | Gj,rₜ | Damped and bounded operational-state factor | – | 42 |  |
| Corrections, energy, and carbon | Ptot,ₜ | Final total electrical power | kW | 43 |  |
| Corrections, energy, and carbon | Eₜ | Electrical energy consumed during one simulation period | kWh | 43–44, 49, 59 |  |
| Corrections, energy, and carbon | MCO₂,ₜ | Operational carbon emissions associated with electricity use | kg CO₂e | 44, 49, 51 |  |
| Corrections, energy, and carbon | EFgrid | Electricity-grid emission factor | kg CO₂e kWh⁻¹ | 44, 49, 51 |  |
| Comfort indicator | Tz,ind,ₜ | Empirical zone-temperature indicator used by the current objective | °C | 45, 47 |  |
| Comfort indicator | kRH,c | Humidity contribution coefficient in the empirical comfort indicator | °C %-point⁻¹ | 45 |  |
| Comfort indicator | Pcap,ₜ | Empirical unmet-capacity temperature penalty | °C | 45–46 |  |
| Comfort indicator | Qunmet,ₜ | Thermal load exceeding available HVAC capacity | kW | 46 |  |
| Comfort indicator | Tset | Nominal comfort reference temperature | °C | 47, 52 |  |
| Comfort indicator | DT,ₜ | Absolute empirical comfort deviation | K | 47, 49 |  |
| S3 optimization | xₜ | S3 control vector [Tsp,ₜ, αₜ]ᵀ | mixed | 48 |  |
| S3 optimization | Tsp,min, Tsp,max | Lower and upper setpoint bounds | °C | 48, 53 |  |
| S3 optimization | αmin, αmax | Lower and upper airflow-fraction bounds | – | 48, 53 |  |
| S3 optimization | ēₜ | Recommended notation for normalized energy objective; replaces eₜ only typographically | – | 49–51 |  |
| S3 optimization | δ̄ₜ | Recommended notation for normalized degradation objective; equal to δₜ in the current code | – | 49–51 |  |
| S3 optimization | D̄ₜ | Recommended notation for normalized comfort-deviation objective | – | 49–51 |  |
| S3 optimization | M̄ₜ | Recommended notation for normalized carbon objective | – | 49–51 |  |
| S3 optimization | wE, wD, wC, wG | Weights assigned to energy, degradation, comfort, and carbon terms | – | 50–51 |  |
| S3 optimization | Jₜ | Weighted S3 objective-function value | – | 50–51 |  |
| S3 optimization | μₖ | Mean/search-centre vector of the Gaussian candidate distribution | mixed | 52–55 |  |
| S3 optimization | σₖ | Standard-deviation vector of the Gaussian candidate distribution | mixed | 52–55 |  |
| S3 optimization | εₖ,i | Standard-normal random candidate vector | – | 53 |  |
| S3 optimization | xₖ,i | Candidate control vector i at iteration k | mixed | 53, 55 |  |
| S3 optimization | Np | Candidate population size | candidate | 54–55 |  |
| S3 optimization | Ne | Number of elite candidates | candidate | 54–55 |  |
| S3 optimization | Niter | Fixed number of stochastic-search iterations | iteration | 55 |  |
| Maintenance and cost | uHX,ₜ | Binary heat-exchanger cleaning decision | 0 or 1 | 56, 58, 60 |  |
| Maintenance and cost | uF,ₜ | Binary filter-replacement decision | 0 or 1 | 57–58, 60 |  |
| Maintenance and cost | Rf,warn | Heat-exchanger fouling warning threshold | m² K W⁻¹ | 56 |  |
| Maintenance and cost | ΔPwarn | Filter pressure-drop warning threshold | Pa | 57 |  |
| Maintenance and cost | δtrig | Composite degradation maintenance trigger | – | 56–57 |  |
| Maintenance and cost | CE,ₜ | Period electricity cost | USD | 59, 61 |  |
| Maintenance and cost | pE | Electricity tariff | USD kWh⁻¹ | 59 |  |
| Maintenance and cost | CM,ₜ | Direct maintenance cost during the period | USD | 60–61 |  |
| Maintenance and cost | CF | Unit cost of filter replacement | USD action⁻¹ | 60 |  |
| Maintenance and cost | CHX | Unit cost of heat-exchanger cleaning | USD action⁻¹ | 60 |  |
| Maintenance and cost | Ctot,ₜ | Total period energy plus maintenance cost | USD | 61 |  |

Important interpretation: The nomenclature table defines symbols, but it does not convert empirical coefficients into literature constants. Coefficients and correction arrays that originate from the code must be reported as calibrated or assumed model parameters.

# 2. Equation-to-reference map

| Equation range | Supporting reference(s) | Honest attribution statement |
| --- | --- | --- |
| 1–18 | ASHRAE (2021); U.S. Department of Energy (2024) | Physical structure is literature-based; reduced-order coefficients and switches are study-specific and require calibration/validation. |
| 19–25 | Bacher and Madsen (2011); U.S. Department of Energy (2024) | RC/state-space concept is supported; the specific two-state discretization, blending fraction, and parameter values are the present model. |
| 26–29 | No external equation source | Empirical monthly availability and minimum-load calibration developed for this study. Report and release all arrays. |
| 30 | Kern and Seaton (1959) | Classical asymptotic fouling form. |
| 31–33 | ASHRAE (2017); Teng et al. (2022) | Dust-loading/pressure-drop relationship is supported; linear dust growth, kclog, and the composite index are study-specific. |
| 34–35 | U.S. Department of Energy (2024); ASHRAE (2021) | Temperature/COP performance-curve concept is supported. Coefficients 0.45, 0.30, 0.018, and 0.010 are empirical model assumptions, not standard coefficients. |
| 36–40 | ASHRAE (2021); U.S. Department of Energy (2024) | Power-balance structure is conventional; monthly floors and degradation multipliers are study-specific. |
| 41–42 | No external equation source | Explicit empirical calibration layers. They must not be described as universal physics. |
| 43 | ASHRAE (2021) | Power-to-energy integration is a dimensional identity. |
| 44 | World Resources Institute and World Business Council for Sustainable Development (2015) | Electricity use multiplied by a grid emission factor. |
| 45–47 | ASHRAE (2023), terminology only | Current equation is an empirical indicator, not PMV, PPD, operative temperature, or Standard 55 compliance. |
| 48–51 | Marler and Arora (2010) | Weighted-sum formulation; current carbon normalization duplicates the energy term under constant EFgrid. |
| 52–55 | Rubinstein (1999), conceptual only | The code is cross-entropy-like but not a formal implementation of the published cross-entropy algorithm. |
| 56–58 | Jardine et al. (2006), classification only | Threshold logic and complete-restoration assumptions are study-specific. |
| 59–61 | Standard engineering cost accounting | Direct algebraic accounting; tariffs and action costs are user/model inputs. |

# 3. APA 7th edition references

American Society of Heating, Refrigerating and Air-Conditioning Engineers. (2021). 2021 ASHRAE handbook—Fundamentals. ASHRAE.

Use in this manuscript: General basis for building loads, heat transfer, infiltration, internal gains, fan/pump concepts, and HVAC design quantities (Eqs. 1–18 and 36–40).

American Society of Heating, Refrigerating and Air-Conditioning Engineers. (2017). ANSI/ASHRAE Standard 52.2-2017: Method of testing general ventilation air-cleaning devices for removal efficiency by particle size. ASHRAE.

Use in this manuscript: Supports the physical relationship among filter dust loading, pressure-drop increase, and final filter resistance. The linear coefficients in Eqs. 31–33 remain study-specific simplifications.

American Society of Heating, Refrigerating and Air-Conditioning Engineers. (2023). ANSI/ASHRAE Standard 55-2023: Thermal environmental conditions for human occupancy. ASHRAE.

Use in this manuscript: Used only to delimit terminology: Eqs. 45–47 are an empirical comfort indicator and are not a Standard 55 PMV/PPD compliance calculation.

Bacher, P., & Madsen, H. (2011). Identifying suitable models for the heat dynamics of buildings. Energy and Buildings, 43(7), 1511–1522. https://doi.org/10.1016/j.enbuild.2011.02.005

Use in this manuscript: Primary basis for lumped RC/grey-box thermal-state modelling (Eqs. 19–25).

Jardine, A. K. S., Lin, D., & Banjevic, D. (2006). A review on machinery diagnostics and prognostics implementing condition-based maintenance. Mechanical Systems and Signal Processing, 20(7), 1483–1510. https://doi.org/10.1016/j.ymssp.2005.09.012

Use in this manuscript: Supports the classification of S3 as condition-based maintenance based on current condition indicators (Eqs. 56–58), rather than forecast-based predictive maintenance.

Kern, D. Q., & Seaton, R. E. (1959). A theoretical analysis of thermal surface fouling. British Chemical Engineering, 4(5), 258–262.

Use in this manuscript: Classical asymptotic fouling-growth basis for Eq. 30.

Marler, R. T., & Arora, J. S. (2010). The weighted sum method for multi-objective optimization: New insights. Structural and Multidisciplinary Optimization, 41(6), 853–862. https://doi.org/10.1007/s00158-009-0460-7

Use in this manuscript: Weighted-sum objective formulation and interpretation of objective weights (Eqs. 49–51).

Rubinstein, R. Y. (1999). The cross-entropy method for combinatorial and continuous optimization. Methodology and Computing in Applied Probability, 1(2), 127–190. https://doi.org/10.1023/A:1010091220143

Use in this manuscript: Conceptual basis for iterative sampling, elite selection, and distribution updating. The implemented routine is only cross-entropy-like and should be named an elite Gaussian stochastic search (Eqs. 52–55).

Teng, G., Shi, G., & Zhu, J. (2022). Influence of pleated geometry on the pressure drop of filters during dust loading process: Experimental and modelling study. Scientific Reports, 12, 20331. https://doi.org/10.1038/s41598-022-24838-7

Use in this manuscript: Experimental/model evidence that pressure drop evolves with deposited dust mass. The simple linear form in Eq. 32 is a reduced-order assumption requiring calibration.

U.S. Department of Energy. (2024). EnergyPlus engineering reference (Version 24.1). EnergyPlus.

Use in this manuscript: Reference framework for zone heat balance, thermostat load calculations, fan power, and performance-curve HVAC modelling (Eqs. 12–25 and 34–40).

World Resources Institute, & World Business Council for Sustainable Development. (2015). GHG Protocol Scope 2 guidance: An amendment to the GHG Protocol corporate standard. World Resources Institute.

Use in this manuscript: Basis for calculating electricity-related operational emissions as activity data multiplied by an emission factor (Eq. 44).

Citation warning. Do not cite the empirical monthly factors, operational-state factors, comfort coefficients, or exact COP-degradation coefficients as though they came from the references above. Those quantities are model-specific and require calibration, sensitivity analysis, and validation.